ES – CD/Aug 2015

HydroThrift Engineering Specifications

(   ) Denotes typical optional features – Edit in accordance with your specific requirements.  Please contact HydroThrift Sales for assistance or additional requirements not included in this specification template.

1.0	Closed Loop Air Cooled Dry-Type Cooling System

1.1	General:  Dry-type closed loop cooling system shall consist of an air-cooled heat exchanger, (trim cooler), and a pump and control unit supplied by HydroThrift Corporation.  The cooling system shall be guaranteed to cool _____ GPM of _____ % (Ethylene Glycol/Water)(Propylene Glycol/Water) from _____F to _____F at _____ F entering design dry bulb temperature.  The closed loop recirculating pump shall re-circulate the flow and produce a total head of _____ ft.

1.2	Heat Exchanger

    - General:  The heat exchanger shall be constructed of seamless copper tubes that are mechanically expanded into corrugated full collared aluminum fins.  The coil assembly shall be supported with dedicated stainless steel tubes to facilitate coil expansion and contraction without wear of the copper heat transfer tubes.  The coil shall be helium leak tested and pneumatically pressure tested to 400 psi.  The cabinet shall be constructed of galvanized steel, which is bolted, riveted, and reinforced by heavy gauge die-formed members.  The heat exchanger shall include direct drive fan(s) with weather protected fan motor(s) incorporating automatic thermal overload protection, copper headers with Outside Diameter Sweat (ODS) connections, and drain and vent valves.  Fan motor(s) shall be wired to a distribution block mounted in a NEMA 3R panel located on the air-cooled heat exchanger.  Fan cycling capacity control shall be located in the control panel on the pump skid.  Fan sections shall be partitioned to prevent air bypass for greater efficiency.  Quiet multi-bladed propeller fan(s) shall provide uniform air distribution throughout the coil surface.  Standard 22” support legs shall be shipped loose with the heat exchanger for field mounting.

1.2.2	(Trim Cooler):  The trim cooler shall be a (plate & frame)(shell & tube) heat exchanger fully mounted and piped onto the pump skid (with a temperature control valve).  The trim cooler shall be designed to cool the liquid, with a cooling water temperature at _____ F, when the max ambient temperature at _____ F exceeds the design dry bulb temperature.

1.3	Pump & Control Unit

1.3.1	General:  The pump and control unit shall consist of a combination vent and surge tank; close-coupled centrifugal circulating pump; (trim cooler); (trim cooler with temperature control valve); (full capacity standby pump); (service valves); and an electrical control panel, all mounted on a structural steel frame with a solid steel deck. All carbon steel piping; one temperature gauge on the supply to the equipment, one temperature gauge on the return from the equipment, each provided with a thermowell; one pump suction pressure gauge, one pump discharge pressure gauge, each provided with a gauge cock; isolation valves for the pump(s); and wiring shall be included within the confines of the pump skid.

1.3.2	Tank:  The vent and surge tank shall be designed with sufficient volume to accommodate the closed loop fluid thermal expansion, shall separate air and liquid, and cushion the surge of water when starting and stopping the system.  The tank shall include a gauge glass, manual vent valve, fill connection, and drain valve.

    - Pump:  The circulating pump shall be a close-coupled centrifugal circulating pump with the impeller, motor speed, and motor power selected such that the pump does not overload the motor anywhere along the manufacturer’s pump curve.  The pump motor shall be (ODP)(TEFC).  The pump shall be piped and installed such that it can be isolated and removed.  The piping shall not induce any stress on the pump.  Each pump shall include isolation valves to allow for pump service with minimum coolant loss.  Ball valves shall be used up to 2” and butterfly valves shall be used for sizes 2.5” and larger.  Butterfly valves 6” and smaller shall be lever operated and butterfly valves 8” and larger shall be gear operated.

    - Piping:  All piping shall be carbon steel with the design and fabrication in compliance with ASME specifications.  Piping construction shall be threaded for 0.50”– 3” nominal pipe size and welded for 4” and larger.  All welding shall be performed using procedures and personnel certified in accordance with ASME Section IX.  All piping that is smaller than 1.25” NPS shall be Schedule 80 ASME SA106 Grade B, piping 1.25” to 2” NPS shall be Schedule 40 ASME SA106 Grade B, and all piping 2.5” NPS and larger shall be Schedule 40 ASME SA53 Grade B.  Class 150 threaded fittings shall meet ASME SA197 and ASME B16.3.  Standard welded fittings shall meet ASME SA234 WPB and ASME B16.9.  Forged steel Class 3000 unions shall be used for piping connections 2” and smaller.  150 lb flanges shall be used for piping connections of 2.5” and larger and shall meet ASME SA105 and ASME B16.5 requirements.

    - (Service Valves):  Service valves shall be installed on the supply and return connections to the customers’ equipment to isolate the customers’ equipment from the pump and control unit.  Ball valves shall be used up to 2” and butterfly valves shall be used for sizes 2.5” and larger.  Butterfly valves 6” and smaller shall be lever operated and butterfly valves 8” and larger shall be gear operated.

    - (Full Capacity Standby Pump):  The pump and control skid shall have a full capacity standby–circulating pump mounted, piped, and wired.  Check valves shall be provided to prevent back flow when either pump is running.  An automatic pump alternator shall be provided to switch operating pumps every time the selector switch is operated or in the event the operating pump motor overload trips.

    - Electrical Control Circuit:  The NEMA (12) (4) electrical enclosure shall include IEC motor starter protectors with an integrated circuit breaker, contactor, and overload protection for the circulating pump(s).  Fan motors shall include individual, automatic thermal overload protection and be grouped and thermostatically operated with a contactor protected by a multipole circuit breaker. A single point 460/3/60 electrical power feed connection to a power distribution block shall be provided.  The control circuit shall include a 115/1/60 control voltage transformer, power on light, (Off-On)(Hand-Off-Auto) selector switch for the circulating pump(s), thermostatic fan cycling controls, and Hand-Off-Auto selector switch for the fan(s).  The electrical panel shall only utilize UL listed or UL recognized electrical components and shall be designed and fabricated in accordance with the latest revision of UL 508A as certified by ETL.

      - (Indicating Lights):  White enclosure lights shall be provided to indicate all energized pump motor(s) and fan motor group(s).

1.3.7.2	(Alarm Horn/Silence Pushbutton):  An audible alarm horn shall be mounted to the electrical enclosure.  The horn shall have a volume adjustment and shall be the same NEMA rating as the electrical enclosure.  A silence push button shall be mounted on the enclosure door.  The horn shall provide audible indications if any of the following alarm conditions occur.  When silenced for one alarm condition, the alarm horn shall sound if another alarm condition occurs.  The silence button shall also reset latched alarm indicating lights after the alarm condition is resolved.

1.3.7.3	(Low Liquid Level Alarm):  A low liquid level alarm system shall be provided to indicate water glycol level has dropped to the bottom of the vent and surge tank sight glass. A solid-state conductance type liquid level control relay shall be provided in the electrical enclosure and an electrode fitting mounted on top of the vent and surge tank.  The electrode fitting shall have a pressure rating of at least 125 psig and include two stainless steel electrode rods.  The liquid level control relay shall include a 6-second time delay.  In the event of a low liquid level condition, a red alarm indicating light shall be illuminated and the optional alarm horn shall sound.

1.3.7.4	(Low Flow Alarm):  A paddle type flow switch shall be provided to indicate a low flow condition.  The flow switch shall have a pressure rating of at least 150 psig.  In the event of a low flow condition, a red alarm indicating light shall be illuminated and the optional alarm horn shall sound.

1.3.7.5	(High Temperature Alarm):  Additional thermostatic control shall be provided to indicate a high equipment supply fluid temperature.  The temperature switch shall alarm at _____F above the design operating temperature.  In the event of a high temperature alarm condition, a red alarm indicating light shall be illuminated and the optional alarm horn shall sound.

      - (Motor Failure Alarm):  Indication of pump motor failure due to an overload condition shall be supplied for all pump motors.  If the overload relay on the motor starter trips, a red alarm indicating light shall be illuminated and the optional alarm horn shall sound.

      - (Main Panel Disconnect Switch):  An enclosure flange mounted disconnect switch shall be provided with means to lock the handle in the OFF position and interrupt power to the entire cooling system.  The disconnect switch mechanism shall also prevent the enclosure door from being opened when in the ON position although means shall also be provided to bypass this mechanism for troubleshooting by a qualified electrical technician.  The operating handle shall operate a circuit breaker switch mounted on the enclosure subpanel.

      - (Pump Motor Disconnect Switch):  All pump motors shall be provided with a NEMA 4 disconnect switch.

      - (Fan Motor Group Disconnect Switch):  All fan motor groups shall be provided with a NEMA 4 disconnect switch.

1.4	Warranty

    - Pump & Control Unit:  The manufacturer’s standard warranty shall be for a period of one year from the date of startup or eighteen months from the date of shipment.

    - Heat Exchanger:  The heat exchanger coil shall be warranted to be free from defects in material and workmanship under normal use and service for a period of three years after date of manufacture.  All other components shall be warranted for a period of one year from start up or eighteen months from shipment, whichever occurs first.