ES – CE/Aug 2015

HydroThrift Engineering Specifications

(   ) Denotes typical optional features – Edit in accordance with your specific requirements.  Please contact HydroThrift Sales for assistance or additional requirements not included in this specification template.

1.0	Closed Loop Evaporative-Type Cooling System

1.1	General:  Evaporative-type closed loop cooling system shall consist of an evaporative style, closed circuit fluid cooler, and a pump and control unit supplied by HydroThrift Corporation.  The cooling system shall be guaranteed to cool _____ GPM of _____ % (Ethylene Glycol/Water)(Propylene Glycol/Water) from _____F to _____F at _____ F entering wet bulb temperature.  The closed loop recirculating pump shall recirculate the flow and produce a total head of _____ ft.

1.2	Fluid Cooler

    - General:  The fluid cooler shall be complete with a (steel coil galvanized for exterior corrosion protection)(copper coil), water basin with strainer, float type water make-up valve, drain, (thermostatically controlled electric basin heater), spray pump(s) with close-coupled TEFC motor(s), water distribution system that uniformly cools the exterior of the coil, fan(s), TEFC fan motor(s), and moisture eliminators, assembled in a heavy gauge galvanized steel casing. Spray pump and fan cycling thermostatic control shall be located in the electrical enclosure on the pump skid.

1.3	Pump & Control Unit

1.3.1	General:  The pump and control unit shall consist of a combination vent and surge tank; close-coupled centrifugal circulating pump; (full capacity standby pump); (service valves); and an electrical control panel, all mounted on a structural steel frame with a solid steel deck. All carbon steel piping; one temperature gauge on the supply to the equipment, one temperature gauge on the return from the equipment, each provided with a thermowell; one pump suction pressure gauge, one pump discharge pressure gauge, each provided with a gauge cock; isolation valves for the pump(s); and wiring shall be included within the confines of the pump skid.

1.3.2	Tank:  The vent and surge tank shall be designed with sufficient volume to accommodate the closed loop fluid thermal expansion, shall separate air and liquid, and cushion the surge of water when starting and stopping the system.  The tank shall include a gauge glass, manual vent valve, fill connection, and drain valve.

    - Pump:  The circulating pump shall be a close-coupled centrifugal circulating pump with the impeller, motor speed, and motor power selected such that the pump does not overload the motor anywhere along the manufacturer’s pump curve.  The pump motor shall be (ODP)(TEFC).  The pump shall be piped and installed such that it can be isolated and removed.  The piping shall not induce any stress on the pump.  Each pump shall include isolation valves to allow for pump service with minimum coolant loss.  Ball valves shall be used up to 2” and butterfly valves shall be used for sizes 2.5” and larger.  Butterfly valves 6” and smaller shall be lever operated and butterfly valves 8” and larger shall be gear operated.

    - Piping:  All piping shall be carbon steel with the design and fabrication in compliance with ASME specifications.  Piping construction shall be threaded for 0.50”– 3” nominal pipe size and welded for 4” and larger.  All welding shall be performed using procedures and personnel certified in accordance with ASME Section IX.  All piping that is smaller than 1.25” NPS shall be Schedule 80 ASME SA106 Grade B, piping 1.25” to 2” NPS shall be Schedule 40 ASME SA106 Grade B, and all piping 2.5” NPS and larger shall be Schedule 40 ASME SA53 Grade B.  Class 150 threaded fittings shall meet ASME SA197 and ASME B16.3.  Standard welded fittings shall meet ASME SA234 WPB and ASME B16.9.  Forged steel Class 3000 unions shall be used for piping connections 2” and smaller.  150 lb flanges shall be used for piping connections of 2.5” and larger and shall meet ASME SA105 and ASME B16.5 requirements.

    - (Service Valves):  Service valves shall be installed on the supply and return connections to the customers’ equipment to isolate the customers’ equipment from the pump and control unit.  Ball valves shall be used up to 2” and butterfly valves shall be used for sizes 2.5” and larger.  Butterfly valves 6” and smaller shall be lever operated and butterfly valves 8” and larger shall be gear operated.

    - (Full Capacity Standby Pump):  The pump and control skid shall have a full capacity standby–circulating pump mounted, piped, and wired.  Check valves shall be provided to prevent back flow when either pump is running.  An automatic pump alternator shall be provided to switch operating pumps every time the selector switch is operated or in the event the operating pump motor overload trips.

    - Electrical Control Circuit:  The NEMA (12) (4) electrical enclosure shall include IEC motor starter protectors with an integrated circuit breaker, contactor, and overload protection for the circulating pump(s), fan motor(s), and spray pump motor(s).  A circuit breaker and contactor shall be provided to power the basin heater, if required.  A single point 460/3/60 electrical power feed connection to a power distribution block shall be provided.  The control circuit shall include a 115/1/60 control voltage transformer, power on light, (Off-On)(Hand-Off-Auto) selector switch for the circulating pump(s), thermostatic fan and spray pump controls, Hand-Off-Auto selector switch for the fan(s) and spray pump(s), and Off-Auto selector switch for the basin heater.  The electrical panel shall only utilize UL listed or UL recognized electrical components and shall be designed and fabricated in accordance with the latest revision of UL 508A as certified by ETL.

      - (Indicating Lights):  White enclosure lights shall be provided to indicate all energized pump, spray pump and fan motor(s) and the basin heater(s), if required.

1.3.7.2	(Alarm Horn/Silence Pushbutton):  An audible alarm horn shall be mounted to the electrical enclosure.  The horn shall have a volume adjustment and shall be the same NEMA rating as the electrical enclosure.  A silence push button shall be mounted on the enclosure door.  The horn shall provide audible indications if any of the following alarm conditions occur.  When silenced for one alarm condition, the alarm horn shall sound if another alarm condition occurs.  The silence button shall also reset latched alarm indicating lights after the alarm condition is resolved.

1.3.7.3	(Low Liquid Level Alarm):  A low liquid level alarm system shall be provided to indicate water glycol level has dropped to the bottom of the vent and surge tank sight glass. A solid-state conductance type liquid level control relay shall be provided in the electrical enclosure and an electrode fitting mounted on top of the vent and surge tank.  The electrode fitting shall have a pressure rating of at least 125 psig and include two stainless steel electrode rods.  The liquid level control relay shall include a 6-second time delay.  In the event of a low liquid level condition, a red alarm indicating light shall be illuminated and the optional alarm horn shall sound.

1.3.7.4	(Low Flow Alarm):  A paddle type flow switch shall be provided to indicate a low flow condition.  The flow switch shall have a pressure rating of at least 150 psig.  In the event of a low flow condition, a red alarm indicating light shall be illuminated and the optional alarm horn shall sound.

1.3.7.5	(High Temperature Alarm):  Additional thermostatic control shall be provided to indicate a high equipment supply fluid temperature.  The temperature switch shall alarm at _____F above the design operating temperature.  In the event of a high temperature alarm condition, a red alarm indicating light shall be illuminated and the optional alarm horn shall sound.

      - (Motor Failure):  Indication of motor failure due to an overload condition shall be supplied for all pump, spray pump, and fan motors.  If the overload relay on the motor starter trips, a red alarm indicating light shall be illuminated and the optional alarm horn shall sound.

      - (Main Panel Disconnect Switch):  An enclosure flange mounted disconnect switch shall be provided with means to lock the handle in the OFF position and interrupt power to the entire cooling system.  The disconnect switch mechanism shall also prevent the enclosure door from being opened when in the ON position although means shall also be provided to bypass this mechanism for troubleshooting by a qualified electrical technician.  The operating handle shall operate a circuit breaker switch mounted on the enclosure subpanel.

      - (Pump Motor Disconnect Switch):  All pump motors shall be provided with a NEMA 4 disconnect switch.

1.4	Warranty

1.4.1	General:  The manufacturer’s standard warranty shall be for a period of one year from the date of startup or eighteen months from the date of shipment, whichever comes first.