SPECIFICATION DATA - Steam Distributing Coils Date:_________Page __ of __

Name: _____________________________________  Company: ___________________________________________

Address : _______________________________________________________________________________________

City, State, Zip :_________________________________   Tele: ___________________   FAX: ___________________

Job Ref: _________________________________  Coil Model No ____________________________    Qty  _________

Dimensional Data						Performance Data

Fin Height (“FH”)A ________  / Finned Length (“FL”) ________  		Heat Load  ____________ BTU/Hr.

Rows Deep (1 or 2)  _______ / Fins Per InchB _______			Airflow  _______________ SCFM or Lbs/ Hr

Casing Height (“CH”)  ______ / Tube Dia. 5/8" or 1" ? _____		Face Velocity  _________  FPM

Casing Length (“CL”) _______ / Casing Depth (“CD”)   ______		Entering Air Temperature   _______  °F

Casing Flange WidthsC:  F1  _________    F2 __________		Leaving  Air Temperature   _______  °F

Over Coil Casing and Header Length (“OL”)  __________		Saturated Steam Pressure  _______  PSIG

Connection Size2&3:Supply   _____ MPT  /  Return _____ MPT		Saturated Steam Temp.  _________  °F

AIR DIRECTION:      Horizontal Airflow    Vertical Airflow		Condensate Flow Rate    _________  Lbs/Hr.

COIL MOUNTING5:  Horizontal Tubes     Vertical Tubes 		Air Friction Pressure Drop  ______ Inches W.G.

Notes:__________________________________________________________________________________________

_______________________________________________________________________________________________

_______________________________________________________________________________________________

_______________________________________________________________________________________________

_______________________________________________________________________________________________

Standard Dimensional Specifications For 5/8¤ OD and 1¤ OD Tubes

|  | A Fin Height | B Fin Spacings | C Flange Widths |  | Connection Size |  | L1 |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Increments | Min - Max | F1 | F2 | Supply | Return | 5/8” O.D. | 1” O.D. |
|  | 3” (on 1” OD) | 4 -12 | 1 1/2” | 1 1/2” | 1 1/2” | 1” | 6” | - |
|  | 1 1/2” (on 5/8” | (Other FPI | (1 1/4” |  | 2” | 1 1/2” | 6 1/2” | 10” |
|  | OD tubes) | Available) | Min.) |  | 3” | 2” | 7” | 10” |

Notes:

1. Indicate direction of supply and return connections if different from above (use separate sheet if necessary).

2. Other connection sizes are optionally available.  Use “L1” dimensions of next larger supply connection size shown.

3. To insure most economical coil, specify connection location dimensions only if critical to the installation.

4. Unless otherwise specified, standard dimension shown apply to 5/8” OD tube coils only.  Consult factory on 1” coils.

5. To insure adequate draining of condensate, coils with horizontal tubes should be installed with a pitch of 1/8” per foot towards   	return connection.  On vertical tube coils, install steam traps on both the supply and return lines.

HydroThrift Corporation                    Tel:   330-837-5141

P.O.Box 1037                                     Fax:  330-837-0558

1301 Sanders Ave SW

Massillon, Ohio   44648          USA

After completed:  FAX to (330) 837-0558 or Email to Sales@HydroThrift.com